## Overview
Tool for optimizing and simulating off- and on-grid electrification solutions
Excel template for input data and simulation settings
This excel-template serves as an input for an oemof-based optimization and simulation tool. The tool has following features:
* Simulation and evaluation based on electrificy flows, with hourly time-resolution
* Easy adaptation of settings and input parameters
* Easy case definition
* Possibility to perform batch analysis of different locations
* Sensitivity analysis of parameters
* Output: Performance and feasibility indicators, energy flows as csv and as png
| Tab | Function
| settings | Simulation settings
| input_constant | Constant input parameters (Definition of base case for sensitivity analysis)
| input_sensitivity | Input parameters subject to the sensitivity analysis
| project_sites | Input data specific to locations
| case_definitions | Case definitions

## settings
Defining settings
| General | Electricity solution settings
| Simulated cases | Cases evaluated
| Oemof settings | Oemof-internal simulation settings
| File settings | File locations
| Output – Files | Data saved to file
| Output – Terminal display | Data is displayed in terminal
| Output – Evaluated values | Simulation/evaluation values added to the result file
| setting_name | setting_value
General
| restore_oemof_if_existant | False
| restore_blackouts_if_existant | False
| include_shortage_penalty_costs_in_lcoe | False
| allow_shortage | True
| evaluated_days | 7
| time_start | 2018-01-01
| time_frequency | H | currently only hourly timestep
| sensitivity_all_combinations | True
| perform_multicriteria_analysis | True
Oemof settings
| solver | cbc
| solver_verbose | False
| cmdline_option | ratioGap | ratioGap, AllowedGap
| cmdline_option_value | 0.03
File settings
| input_folder_timeseries | ./inputs/timeseries | for timeseries
| output_folder | simulation_results
| output_file | test_result1
Output – files
| save_lp_file | False
| lp_file_for_only_3_timesteps | False | This will perform whole simulation with only 3 timesteps!
| save_oemofresults | False
| save_to_csv_flows_storage | False
| save_to_csv_flows_electricity_mg | False
| save_to_png_flows_storage | False
| save_to_png_flows_electricity_mg | True
Output – Terminal display
| display_meta | False
| display_main | False
| display_experiment | False
Output – Evaluated values
| results_demand_characteristics | True
| results_blackout_characteristics | True
| results_annuities | True
| results_costs | True

## input_constant
Definition of constant input parameters
Doubled values | Make sure that the sensitivity setting fits the experiments you want to simulate – either sensitivity or project site values may be preffered
Missing values | Tab “data_sufficiency_check” helps to identify missing /doubled data, but is by no means a thourough check. Python error messages will occur if values are left undefined
Parameter | Value | Unit
blackout_duration | 0 | hrs
blackout_duration_std_deviation | 0 | fraction
blackout_frequency | 0 | /mth
blackout_frequency_std_deviation | 0 | fraction
combustion_value_fuel | 9.8 | kWh/l
demand_ac_scaling_factor | 1 | factor
demand_dc_scaling_factor | 1 | factor
distribution_grid_cost_investment | 0 | currency
distribution_grid_cost_opex | 0 | /a
distribution_grid_lifetime | 40 | a
genset_batch | 0.5 | kW
genset_cost_investment | 820 | /kW
genset_cost_opex | 0.05 | /kW/a
genset_cost_var | 0 | /kWh
genset_efficiency | 0.33 | factor
genset_lifetime | 10 | a
genset_max_loading | 1 | fraction
genset_min_loading | 0.1 | fraction
genset_oversize_factor | 1 | factor | (only used if estimated through case definition “peak demand”)
inverter_dc_ac_batch | 0.5 | kW
inverter_dc_ac_cost_investment | 0 | /kW
inverter_dc_ac_cost_opex | 0 | /kW/a
inverter_dc_ac_cost_var | 0 | /kWh
inverter_dc_ac_efficiency | 1 | fraction
inverter_dc_ac_lifetime | 15 | a
maingrid_distance | 1 | km
maingrid_electricity_price | 0.08 | /kWh
maingrid_extension_cost_investment | 0 | /km
maingrid_extension_cost_opex | 0 | /km/a
maingrid_extension_lifetime | 40 | a
maingrid_feedin_tariff | 0.05 | /kWh
maingrid_renewable_share | 0 | fraction
min_renewable_share | 0 | fraction
pcoupling_batch | 1 | kW
pcoupling_cost_investment | 200 | /kW
pcoupling_cost_opex | 0 | /kW/a
pcoupling_cost_var | 0 | /kWh
pcoupling_efficiency | 1 | fraction
pcoupling_lifetime | 20 | a
pcoupling_oversize_factor | 1.5 | factor | (only used if estimated through case definition “peak demand”)
fuel_price | 0.68 | /l
fuel_price_change_annual | 0.05 | p.a.
project_cost_investment | 20000 | currency
project_cost_opex | 0 | /a
project_lifetime | 20 | a
pv_batch | 0.5 | kWp
pv_cost_investment | 1250 | /kWp
pv_cost_opex | 25 | /kWp/a
pv_cost_var | 0 | /kWh
pv_lifetime | 25 | a
rectifier_ac_dc_batch | 0.5 | kW
rectifier_ac_dc_cost_investment | 0 | /kW
rectifier_ac_dc_cost_opex | 0 | /kW/a
rectifier_ac_dc_cost_var | 0 | /kWh
rectifier_ac_dc_efficiency | 1 | fraction
rectifier_ac_dc_lifetime | 15 | a
shortage_max_allowed | 0 | fraction
shortage_max_timestep | 1 | fraction
shortage_penalty_costs | 0.5 | /kWh
stability_limit | 0.2 | fraction
storage_batch_capacity | 1 | kWh
storage_batch_power | 1 | kWh
storage_capacity_cost_investment | 250 | /kWh
storage_capacity_cost_opex | 6.75 | /kWh/a
storage_capacity_lifetime | 13.5 | a
storage_cost_var | 0 | a
storage_Crate_charge | 1 | fraction
storage_Crate_discharge | 0.5 | fraction
storage_efficiency_charge | 0.97 | fraction
storage_efficiency_discharge | 0.97 | fraction
storage_loss_timestep | 0 | fraction
storage_power_cost_investment | 500 | /kW
storage_power_cost_opex | 0 | /kW/a
storage_power_lifetime | 13.5 | a
storage_soc_initial | None | None or factor
storage_soc_max | 1 | fraction
storage_soc_min | 0.2 | fraction
tax | 0 | fraction
wacc | 0.16 | fraction
white_noise_demand | 0 | fraction
white_noise_pv | 0 | fraction
white_noise_wind | 0 | fraction
wind_batch | 0.5 | kW
wind_cost_investment | 1100 | /kW
wind_cost_opex | 0 | /kW/a
wind_cost_var | 0 | /kWh
wind_lifetime | 20 | a
fuel_co2_emission_factor | 2.68 | kgCO2eq/l
maingrid_co2_emission_factor | 0.9 | kgCO2eq/kWh

## input_sensitivity
Definition of sensitivity parameters
Deleting rows | Rows can be deleted. Remember to check if the deleted value is defined in input_constant or project_sites
Doubled values | Make sure that the sensitivity setting fits the experiments you want to simulate – either sensitivity or project site values may be preffered
Parameter | Parameter from input_costant that is subject to sensitivity analysis
Min | Minimal value of parameter
Max | Maximal value of parameter
Step | Step lenght for values between min and max value of parameter
Parameter | Min | Max | Step
storage_capacity_cost_investment | 200 | 500 | 20

## project_sites
Definition of project locations
Number of locations | An unlimited number of locations can be added below. Make sure that project site names are only used once
Necessary entries | For each project location: project_site_name, timeseries_file, title_time, title_demand, title_pv, title_wind, title_grid_availability, seperator
Additional columns | Project site specific can be defined in additional columns. If one project has a specific value, the value needs to be defined here for all project sites
timeseries_file | The timeseries have to be provided in an external csv file.
title_time | Title of column with timestamp or None
title_demand | Title of column with demand in kW
title_pv | Title of column with PV generation in kW/kWp, or None
title_wind | Title of column with wind generation in kW/kW, or None
title_grid_availability | Title of column with grid availability (boolean) or None
seperator | Seperator used in csv file
project_site_name | timeseries_file | title_time | title_demand_ac | title_demand_dc | title_pv | title_wind | title_grid_availability | seperator
test_site | test_site.csv | None | Demand | None | SolarGen | Wind | None | ;

## case_definitions
Case definitions
Adding cases | An unlimited number of cases can be added in new columns. Make sure each has an unique name.
case_name | string
based_on_case | False or True
pv_fixed_capacity | oem, string (name of base capacity case), None
storage_fixed_capacity | oem, string (name of base capacity case), None
genset_fixed_capacity | oem, string (name of base capacity case), None, peak_demand
pcc_consumption_fixed_capacity | oem, string (name of base capacity case), None
pcc_feedin_fixed_capacity | oem, string (name of base capacity case), None
allow_shortage | True or False
max_shortage | value, default (recommended)
stability_constraint | False, share_usage, share_backup, share_hybrid (recommended)
renewable_constraint | True or False or default
tariff for electrical service | Value if known, else None
case_name | diesel_mg | pv-diesel-mg | pv-diesel-storage-mg | pv-wind-storage-diesel-mg
perform_simulation | True | True | True | False
based_on_case | False | False | True | True
capacity_pv_kWp | None | oem | oem | oem
capacity_wind_kW | None | None | None | oem
capacity_storage_kWh | None | None | oem | oem
force_charge_from_maingrid | False | False | False | False
discharge_only_when_blackout | False | False | False | False
capacity_rectifier_ac_dc_kW | oem | oem | oem | oem
capacity_inverter_dc_ac_kW | oem | oem | oem | oem
enable_inverter_only_at_backout | False | False | False | False
capacity_genset_kW | oem | oem | oem | oem
genset_with_minimal_loading | False | False | False | False
number_of_equal_generators | 1 | 1 | 1 | 1
capacity_pcc_consumption_kW | None | None | None | None
capacity_pcc_feedin_kW | None | None | None | None
allow_shortage | True | True | True | True
max_shortage | default | default | default | default
stability_constraint | share_hybrid | share_hybrid | share_hybrid | share_hybrid
renewable_constraint | False | False | False | False
tariff for electrical service | None | None | None | None
evaluation_perspective | AC_system | AC_system | AC_system | AC_system

## multicriteria_data
Multicriteria analysis
Weighting | Dimensions and criteria must be weighted
Dimension | The sum of the weights of all dimensions must equal 1.
Criteria | The sum of the weights of the criteria belonging to each dimension must equal 1
Technology assessment | Punctuations of 1-4 (1 for weak performance, 4 for good performance) must be given to each generation source for the qualitative criteria. None if a source is not considered.
Plot | Plot results of the criterion evaluation (True or False)
Show results of sensibility | Choose which parameters are considered in the multicriteria analysis (True or False). All combinations in settings ta bmust be selected to display the combinations correctly
Dimensions | weight
economic | 0.28623
technical | 0.25807
socioinstitutional | 0.23396
environmental | 0.22174
Tecnology assessment
Dimensions | Abrev | Criteria | weight | pv | wind | diesel | maingrid | plot
Economic | EC1 | Initial investment | 0.51389 |  |  |  |  | FALSE
| EC2 | O&M costs | 0.48611 |  |  |  |  | FALSE
Technical | T1 | Autonomy factor | 0.25987 |  |  |  |  | FALSE
| T2 | Complete fulfillment of demand | 0.23849 |  |  |  |  | FALSE
| T3 | Reliabilty of supply | 0.24683 | 2.75 | None | 1.88 | 3 | FALSE
| T4 | Equipment failure | 0.25481 | 2.25 | None | 1.5 | 3 | FALSE
Social | S1 | Users acceptance | 0.26535 | 2 | None | 2.6 | 2.17 | TRUE
| S2 | Tariff for electric service | 0.39644 |  |  |  |  | FALSE
| S3 | Institutional alignment | 0.3382 | 2.57 | None | 1.71 | 2.14 | TRUE
Environmental | EN1 | CO2 emissions | 0.25581 | 0 | None | 0.77 | 0.44 | FALSE | kgCO2/kWh: https://ecometrica.com/assets/Electricity-specific-emission-factors-for-grid-electricity.pdf
| EN2 | Impact on population | 0.38378 | 2.63 | None | 1 | 1.88 | FALSE
| EN3 | Wastes of components | 0.36042 | 1.63 | None | 1.5 | 2.63 | TRUE
Show results of sensibility
parameter | show
#REF! | TRUE
#REF! | TRUE